# CEMS Digital Twin v5: A Multi-Scale Simulation Platform for 100 MW AI Data Center Renewable Microgrids

Technical Document — For Demonstration and Publication

Version: DT5 | Date: 2026-03-02 | Validation: 92/92 tests passing

────────────────────────────────────────────────────────────

## Abstract

This document presents CEMS Digital Twin v5, a comprehensive simulation platform for the design, operation, and investment analysis of a 100 MW-class AI Data Center (AIDC) integrated with a renewable microgrid. The platform comprises 13 core modules and 3 expansion modules spanning photovoltaic (PV) generation, a 6-layer Hybrid Energy Storage System (HESS), hydrogen power-to-gas-to-power, a 3-tier AI Energy Management System (AI-EMS), carbon accounting (Scope 1/2/3), grid interface, and economic optimization. The system supports multi-scale temporal resolution from 1 ms (power electronics) to 1 year (economic analysis) using a lumped-parameter spatial model. Key innovations include: (i) frequency-based load separation across 6 storage technologies (supercapacitor through seasonal H₂ storage); (ii) LP-based optimal dispatch with SOC-adaptive merit order; and (iii) Monte Carlo sensitivity analysis (10,000 iterations) with explicit uncertainty quantification. Validation against an advisory board review achieved a B+ to A− rating with all 92 test cases passing. International benchmarking across 5 countries (Korea, USA, China, Japan, Germany) contextualizes the platform within the global AIDC energy landscape.

Keywords: Digital Twin, AI Data Center, Renewable Microgrid, Hybrid Energy Storage, Hydrogen, Energy Management System, Techno-Economic Analysis

────────────────────────────────────────────────────────────

## Table of Contents

[Introduction](#1-introduction)

[System Architecture](#2-system-architecture)

[Methodology](#3-methodology)

3.1 PV Generation Model (M1)

3.2 Hybrid Energy Storage System (M2)

3.3 AIDC Load Model (M3)

3.4 DC Bus Power Distribution (M4)

3.5 Hydrogen System (M5)

3.6 AI Energy Management System (M6)

3.7 Carbon Accounting (M7)

3.8 Grid Interface (M8)

3.9 Economic Optimization (M9)

3.10 Weather Module (M10)

3.11 Policy Simulator (M11)

3.12 Industry Commercialization (M12)

3.13 Investment Dashboard (M13)

[Data Sources](#4-data-sources)

[Validation and Results](#5-validation-and-results)

[Discussion](#6-discussion)

[Conclusions](#7-conclusions)

[References](#8-references)

────────────────────────────────────────────────────────────

## 1. Introduction

The rapid expansion of AI data centers poses significant challenges to power grid infrastructure and sustainability targets. A single 100 MW AIDC consumes approximately 700 GWh annually — equivalent to a mid-sized city — while facing increasingly stringent RE100 commitments and emerging carbon border adjustment mechanisms (EU CBAM). This work presents CEMS Digital Twin v5, a simulation platform that integrates renewable generation, multi-technology energy storage, hydrogen power-to-gas-to-power, and AI-driven energy management to address these challenges.

The key contributions are:

Multi-scale simulation: 1 ms to 1 year temporal resolution within a unified framework

6-layer HESS: Frequency-based load separation across supercapacitor, Li-ion, Na-ion, vanadium RFB, CAES, and H₂ storage

3-tier AI-EMS: Real-time control (1 ms), predictive dispatch (15 min, LP-based), and strategic optimization (1 hr)

Transparent economic analysis: Monte Carlo (10,000 iterations) with explicit uncertainty bounds, adhering to a "no-exaggeration principle"

International benchmarking: 5-country comparison (KR, US, CN, JP, DE) with traceable data sources

────────────────────────────────────────────────────────────

## 2. System Architecture

The platform consists of 13 core modules organized in a hierarchical structure:

Supply side: M1 (PV), M10 (Weather)

Demand side: M3 (AIDC Load)

Storage: M2 (HESS), M5 (H₂)

Distribution: M4 (DC Bus), M8 (Grid Interface)

Control: M6 (AI-EMS)

Analysis: M7 (Carbon), M9 (Economics), M11 (Policy), M12 (Industry), M13 (Investment)

### Simulation Configuration

| Parameter | Value | Application |
| --- | --- | --- |
| Minimum time resolution | 1 ms | Power electronics (HESS supercapacitor) |
| Control resolution | 1 s / 15 min / 1 hr | HESS / Tier 2 dispatch / Tier 3 strategy |
| Simulation horizon | 8,760 hr (1 year) | Annual energy balance |
| Spatial model | Lumped parameter | — |

────────────────────────────────────────────────────────────

## 3. Methodology

### 3.1 PV Generation Model (M1)

The PV module supports four cell technologies: crystalline silicon (c-Si), tandem perovskite/Si, triple-junction III-V, and infinite-junction (theoretical). An emerging "Solar Battery" pathway for direct solar-to-hydrogen conversion is also included.

#### Cell Temperature (NOCT Model)

T_{cell} = T_{amb} + \frac{NOCT - 20}{800} \cdot G \cdot f_{wind} where $f_{wind} = 1 - 0.04 \cdot \max(0, v_{wind} - 2)$ accounts for convective cooling, $G$ is the global horizontal irradiance (W/m²), and $NOCT$ is the nominal operating cell temperature (°C). #### Temperature-Dependent Efficiency (IEC 61215 / IEC 61853) \eta(T) = \eta_{STC} \left[1 + \beta_{rel} \cdot (T_{cell} - 25)\right]

where \eta_{STC} is the efficiency at Standard Test Conditions (25°C, 1000 W/m², AM1.5G), and \beta_{rel} is the relative temperature coefficient (1/°C). The config parameter beta is in %/°C, hence \beta_{rel} = \beta / 100.

| Technology | \eta_{STC} (%) | \beta (%/°C) | NOCT (°C) | Degradation (%/yr) | Area (ha/100 MW) |
| --- | --- | --- | --- | --- | --- |
| c-Si | 24.4 | −0.35 | 45 | 0.5 | 93 |
| Tandem | 34.85 | −0.25 | 43 | 0.8 | 55 |
| Triple | 39.5 | −0.20 | 42 | 1.0 | 48 |
| Infinite | 68.7 | −0.15 | 40 | 0.5 | 28 |

Ref: De Soto et al., Solar Energy 80(1), 2006; IEC 61215:2021; IEC 61853-1:2011.

#### Degradation Model

\eta(t) = \eta_0 \cdot (1 - \delta/100)^t #### Power Output P_{PV} = \frac{\eta}{100} \cdot A_{total} \cdot G \cdot 10^{-6} \quad [\text{MW}]

With active control (MPPT optimization), an additional 5–15% improvement is modeled based on irradiance level.

#### Solar Battery H₂ Production (2030+ Emerging, TRL 2–3)

A water-soluble polymer captures sunlight as chemical energy and releases H₂ on demand (Ref: Nature Communications, DOI:10.1038/s41467-026-68342-2).

\text{STH} = \eta_{capture} \times \eta_{H_2} \times (1 - 0.005d) \times (1 - 0.02t) where $\eta_{capture} = 0.80$, $\eta_{H_2} = 0.72$, yielding a theoretical STH of 57.6% under ideal conditions. This figure represents the product of two sequential process efficiencies and is not directly comparable to conventional PEC/PV-electrolysis STH (~20%). Conservative scenarios (30–40%) are included in the analysis. --- ### 3.2 Hybrid Energy Storage System (M2) #### 6-Layer Architecture | Layer | Technology | Capacity | Power Rating | Response Time | η (charge/discharge) | Time Constant | CAPEX ($/kWh) | |-------|-----------|----------|-------------|--------------|---------------------|---------------|---------------| | L1 | Supercapacitor | 50 kWh | 10 MW | 1 μs | 98/98% | μs–s | 10,000 | | L2 | Li-ion BESS | 2,000 MWh | 200 MW | 100 ms | 95/95% | s–hr | 200 | | L3 | Na-ion BESS | 1,000 MWh | 100 MW | 200 ms | 92/92% | hr–12 hr | 80 | | L4 | Vanadium RFB | 750 MWh | 50 MW | 1 s | 85/85% | hr–day | 300 | | L5 | CAES | 1,000 MWh | 100 MW | 30 s | 75/75% | day–week | 100 | | L6 | H₂ Storage | 5,000 MWh | 50 MW | 5 min | 40/40% | day–season | 20 | **Total storage capacity: ~10 GWh** Na-ion BESS (L3): Hard carbon anode, layered oxide cathode (CATL Naxtra architecture). Key advantages include wide operating temperature range (−40°C to +60°C) and ~10,000 cycle life (2× Li-ion). CAPEX of $80/kWh is a 2026 target; conservative range is $80–$120/kWh. Ref: *Nature Reviews Materials* (2025), doi:10.1038/s41578-025-00857-4. #### Frequency-Based Power Allocation Each layer $i$ is assigned a frequency band $[f_{min,i}, f_{max,i}]$ derived from its time constant range $[\tau_{min,i}, \tau_{max,i}]$: f_{min,i} = 1/\tau_{max,i}, \quad f_{max,i} = 1/\tau_{min,i}

Power requests are allocated in priority order: L1 → L2 → L3 → L4 → L5 → L6. Unallocated power (when the request frequency falls outside all layer bands) is explicitly tracked via _unallocated_kw to ensure energy conservation.

#### SOC Update

Charging: SOC_{new} = SOC + P \cdot \Delta t \cdot \eta_{ch} / (3600 \cdot C_{eff})

Discharging: SOC_{new} = SOC - P \cdot \Delta t / (3600 \cdot C_{eff} \cdot \eta_{dis})

where C_{eff} = C_{rated} \cdot D_f is the degradation-adjusted effective capacity. Self-discharge is applied multiplicatively: SOC \leftarrow SOC \cdot (1 - \sigma \cdot \Delta t / 3600).

#### Degradation Model

D_f = \max\left(0.5, \min(D_{cycle}, D_{temp})\right) - $D_{cycle} = 1 - k_{cycle} \cdot N_{cycle}$ (cycle degradation) - $D_{temp} = 1 - k_{temp} \cdot \max(0, (T - 25)/10)$ (Arrhenius temperature degradation) #### Energy Conservation Verification The `operate_hess()` method returns an energy conservation validation block: E_{requested} = E_{delivered} + E_{unallocated} + E_{loss}

────────────────────────────────────────────────────────────

### 3.3 AIDC Load Model (M3)

The AIDC load model generates stochastic hourly and minute-resolution power demand profiles based on GPU type, count, PUE tier, and workload mix.

Total facility power:

P_{total} = N_{GPU} \cdot P_{GPU} \cdot U(t) \cdot (1 + r_{IT}) \cdot PUE where $U(t)$ is the time-varying GPU utilization, $r_{IT} = 0.12$ (additional IT load ratio), and $PUE$ is the Power Usage Effectiveness. | Workload | Base Utilization | Peak | Burst Freq. (/hr) | Pattern | |----------|-----------------|------|-------------------|---------| | LLM Inference | 55% | 98% | 10 | Diurnal, Poisson arrival | | AI Training | 85% | 100% | 2 | Sustained + 30 min checkpoint | | MoE | 40% | 95% | 20 | Irregular expert activation | Ref: Google TPU workload characterization; Meta LLaMA 3 GPU failure analysis; MLPerf benchmark. --- ### 3.4 DC Bus Power Distribution (M4) The 380V DC Bus manages instantaneous power balance among all subsystems with SiC (default) or GaN (advanced) power converters. **Converter Efficiencies**: | Path | SiC | GaN | |------|-----|-----| | PV → DC Bus | 98.5% | 99.5% | | DC Bus ↔ BESS | 97.5% | 99.0% | | DC Bus → Electrolyzer | 97.0% | 98.5% | | Fuel Cell → DC Bus | 97.0% | 98.5% | | DC Bus → AIDC | 96.0% | 98.0% | | Grid (bidirectional) | 97.0% | 98.5% | **Merit order for surplus**: BESS charge → H₂ electrolysis → Grid export → Curtailment **Merit order for deficit**: BESS discharge → Fuel cell → Grid import → Load shedding (emergency) **Energy balance constraint**: \sum P_{supply,j} \cdot \eta_{supply,j} = \sum P_{demand,k} / \eta_{demand,k}

────────────────────────────────────────────────────────────

### 3.5 Hydrogen System (M5)

#### System Configuration

| Component | Rating | Efficiency (LHV) | Operating Temp. | Startup Time |
| --- | --- | --- | --- | --- |
| PEM Electrolyzer | 50 MW | 65% | 80°C | 15 min |
| PEM Fuel Cell | 50 MW | 55% | 80°C | 5 min |
| H₂ Storage | 150 ton, 350 bar | 95% (compression) | — | — |

Ref: IRENA Green Hydrogen Cost Reduction 2024 (electrolyzer); DOE Hydrogen Program Record 2024 (fuel cell).

#### Round-Trip Efficiency

\eta_{RT} = \eta_{elec} \times \eta_{FC} = 0.65 \times 0.55 = 35.75\% The config value of 37.5% includes BOP (Balance of Plant) correction. Ref: IEA Global Hydrogen Review 2023. CHP mode: $\eta_{RT,CHP} = 82.5\%$ (with 80–85% waste heat recovery). #### Electrochemical Model Nernst voltage: E(T, p) = E_0 + \frac{\Delta S}{2F}(T - 298.15) + \frac{RT}{2F}\ln(p)

where E_0 = 1.229 V, F = 96,485.33 C/mol, R = 8.3145 J/(mol·K).

Electrolyzer efficiency:

\eta_{elec} = \min\left(\eta_{nominal}, \; \eta_{Faraday} \cdot \eta_{voltage} \cdot f_{thermal} \cdot D_f\right) H₂ production: $m_{H_2} = P \cdot \Delta t \cdot \eta_{elec} / HHV_{H_2}$, where $HHV_{H_2} = 39.39$ kWh/kg. #### BNEF 2025 Green H₂ LCOH by Country ($/kg) | Country | LCOH | Country | LCOH | |---------|------|---------|------| | China | 3.2 | Texas, US | 6.5 | | Saudi Arabia | 3.9 | Germany | 8.0 | | India | 5.0 | **Korea** | **8.5** | | Spain | 5.9 | Japan | 10.2 | Source: BloombergNEF 2025 Hydrogen Levelized Cost Report. --- ### 3.6 AI Energy Management System (M6) #### 3-Tier Control Architecture | Tier | Function | Interval | Method | |------|----------|----------|--------| | Tier 1 | Real-time control | 1 ms | MPPT tracking (99%), DC bus stabilization (380V ±2%), HESS dispatch | | Tier 2 | Predictive dispatch | 15 min | LP optimization (scipy.optimize.linprog), 4-hr PV/load forecast | | Tier 3 | Strategic optimization | 1 hr | 24-hr schedule, economic dispatch, maintenance planning | #### Tier 2 LP Formulation **Decision variables** ($n = 8$): PV→AIDC ($x_0$), PV→HESS ($x_1$), PV→Grid ($x_2$), H₂ electrolyzer ($x_3$), HESS→AIDC ($x_4$), H₂ FC ($x_5$), Grid→AIDC ($x_6$), Curtailment ($x_7$). **Objective**: Minimize net cost $c^T x$ with SOC-adaptive cost coefficients: - $c_0 = -P_{grid}$ (self-consumption: maximum savings) - $c_1 = -P_{grid} \cdot \max(0, 1.2 - SOC_{HESS})$ (charge incentive inversely proportional to SOC) - $c_6 = P_{grid}$ (grid purchase: last resort) **Constraints**: - PV balance: $x_0 + x_1 + x_2 + x_3 + x_7 = P_{PV}$ - Load balance: $x_0 + x_4 + x_5 + x_6 = P_{load}$ The LP solver (HiGHS via scipy) ensures optimal dispatch under physical constraints. A rule-based fallback is provided for solver failure. --- ### 3.7 Carbon Accounting (M7) Following the GHG Protocol framework: **Scope 1** (Direct emissions): PEM electrolysis produces zero direct emissions. Diesel backup: $E_{S1} = V_{diesel} \times 2.68 \times 10^{-3}$ tCO₂. **Scope 2** (Indirect, electricity): $E_{S2} = Q_{grid} \times EF_{grid}$, where $EF_{grid} = 0.4594$ tCO₂/MWh (Korea, 2024). **Scope 3** (Supply chain): Annualized manufacturing emissions: E_{S3} = \frac{C_{PV} \times 40 + C_{BESS} \times 65 + C_{H_2} \times 30}{T_{life}} \quad [\text{tCO}_2/\text{yr}]

Avoided emissions: E_{avoided} = Q_{self} \times EF_{grid}

Net emissions: E_{net} = E_{S1} + E_{S2} + E_{S3} - E_{avoided}

K-ETS and EU CBAM cost calculations are integrated with scenario analysis for carbon prices ranging from 25,000 to 100,000 ₩/tCO₂.

────────────────────────────────────────────────────────────

### 3.8 Grid Interface (M8)

The grid interface module manages bidirectional power exchange with the Korean Electric Power Corporation (KEPCO) grid.

Protection settings: Overvoltage 1.1 p.u., undervoltage 0.9 p.u., over-frequency 50.5 Hz, under-frequency 49.5 Hz, minimum power factor 0.95, reconnection delay 300 s.

Frequency response (droop control): \Delta P = -(P_{rated}/(\delta \cdot f_0)) \cdot \Delta f, with \delta = 5\%, deadband ±0.02 Hz.

SMP pricing: Base 80,000 ₩/MWh with seasonal hourly multipliers (summer peak 1.50× at 15:00, off-peak 0.60× at 03:00).

────────────────────────────────────────────────────────────

### 3.9 Economic Optimization (M9)

#### CAPEX Structure

Energy infrastructure (incremental over BAU): 10,000 billion KRW (≈ $7.4B USD)

| Component | CAPEX (B KRW) |
| --- | --- |
| PV 100 MW | 1,500 |
| BESS 2 GWh | 4,000 |
| Supercapacitor | 500 |
| H₂ System | 3,000 |
| DC Bus + converters | 500 |
| Grid interface | 200 |
| AI-EMS | 300 |
| Total (energy infra) | 10,000 |

Note: AIDC facility cost (12,500 B KRW) is excluded as it is identical in the BAU scenario.

#### Financial Metrics

NPV = -CAPEX + \sum_{t=1}^{T} \frac{CF_t}{(1+r)^t}, \quad r = 5\%, \; T = 20 \text{ yr} LCOE = \frac{\sum_{t=0}^{T}(CAPEX_t + OPEX_t)/(1+r)^t}{\sum_{t=1}^{T}E_t/(1+r)^t}

#### Revenue Model

Base revenue streams: electricity self-consumption savings (80,000 ₩/MWh), surplus export at SMP (70,000 ₩/MWh), REC revenue (25,000 ₩/MWh × 1.2 weight), and carbon credits (25,000 ₩/tCO₂).

Additional revenue (630 B KRW/yr): demand charge reduction (280 B, Ref: KEPCO tariff 2024), grid reliability value (220 B, Ref: EPRI Value of DER 2023), and BESS arbitrage (130 B, Ref: Lazard LCOS 2024, KPX 2024). Detailed derivations are documented in the configuration file.

#### Learning Curves

| Technology | Annual cost reduction | 20-year cost ratio |
| --- | --- | --- |
| PV | −7%/yr | 23% |
| BESS | −10%/yr | 12% |
| H₂ | −8%/yr | 19% |

#### Monte Carlo Simulation (10,000 iterations)

| Variable | Std. Dev. (%) | Distribution |
| --- | --- | --- |
| PV efficiency | 5 | Normal (clipped 50–150%) |
| Electricity price | 15 | Normal (clipped 50–200%) |
| Carbon price | 20 | Normal (clipped 30–300%) |
| Discount rate | 10 | Normal (clipped 50–200%) |
| Load variation | 10 | Normal (clipped 70–130%) |

Limitation: Normal distribution with clipping may underestimate tail risks. Log-normal or jump-diffusion models would be more appropriate for energy/carbon prices. Current results should be interpreted as conservative.

────────────────────────────────────────────────────────────

### 3.10 Weather Module (M10)

Synthetic TMY data for central Korea (Seoul, 37.5°N, 127.0°E):

Annual GHI: 1,350 kWh/m² (Ref: KMA TMY3)

Monthly patterns: Peak in May (normalized 1.0), minimum in December (0.4)

Monsoon effect: July cloud probability 70%

Temperature range: −2°C (January) to +28°C (August)

────────────────────────────────────────────────────────────

### 3.11 Policy Simulator (M11)

Scenario analysis for: K-ETS carbon price (25k–100k ₩/tCO₂), REC market, EU CBAM, RE100 targets, national power plan renewable ratio, and the 2026 White House Ratepayer Protection Pledge (80% self-generation requirement).

────────────────────────────────────────────────────────────

### 3.12 Industry Commercialization (M12)

CSP-specific analysis for 4 Korean operators (Samsung Pyeongtaek 500 MW, SK Icheon 300 MW, Naver Sejong 200 MW, Kakao Ansan 100 MW) plus global hyperscaler strategy comparison (Google, Amazon, Meta, Microsoft).

Scaling model: C(S) = C_{100} \cdot (S/100)^{0.85} (power law economies of scale).

────────────────────────────────────────────────────────────

### 3.13 Investment Dashboard (M13)

Go/No-Go decision matrix: IRR ≥ 5%, NPV ≥ 0, Payback ≤ 15 yr, P(NPV > 0) ≥ 50%.

4/4 Pass → GO

3/4 Pass → CONDITIONAL GO

≤ 2/4 Pass → NO-GO

────────────────────────────────────────────────────────────

## 4. Data Sources

### International Data Sources

| Category | Sources |
| --- | --- |
| Weather/Solar | KMA TMY3 (Korea), NREL NSRDB (US), CMA TRY (China), JMA AMeDAS (Japan), DWD TRY (Germany) |
| Electricity prices | KEPCO (Korea), EIA (US), NDRC (China), METI (Japan), Destatis (Germany) |
| Carbon markets | K-ETS (Korea), EU-ETS/ICE ECX, Shanghai EEX, Ember Climate API |
| Technology costs | NREL ATB 2024, IRENA RENEWCOST, Fraunhofer ISE, BNEF H₂ LCOH, Lazard LCOS 2024 |
| Grid emission factors | KPX (Korea), EPA eGRID (US), MEE (China), MOE (Japan), UBA (Germany) |

Benchmark API sources support quarterly/annual automated updates (Ember Climate, NREL ATB, IRENA). Last updated: 2026-02-22.

────────────────────────────────────────────────────────────

## 5. Validation and Results

### 5.1 Test Coverage

92/92 tests passing across all 13 modules + expansion modules + Solar Battery pathway (as of 2026-03-02).

### 5.2 Advisory Board Review

An advisory board review was conducted with three perspectives: Skeptic (physics/engineering fundamentals), Enterprise (business viability), and Arbiter (synthesis).

Must-Fix items resolved:

| ID | Issue | Resolution |
| --- | --- | --- |
| MF-1 | PV temperature coefficient annotation ambiguity | Explicit relative vs. absolute coefficient documentation with IEC references |
| MF-2 | HESS unallocated power energy conservation | Added _unallocated_kw tracking and energy balance verification |
| MF-3 | H₂ RT efficiency config–model inconsistency | Unified to PEM basis (65% × 55% = 35.75%, config 37.5% with BOP) |
| MF-4 | Undocumented additional revenue (630 B KRW) | Detailed derivation with KEPCO, EPRI, KPX, Lazard references |

Overall rating: B+ → A− (post-correction)

### 5.3 International Benchmark

| Country | PV Type | GHI (kWh/m²/yr) | Elec. Price ($/MWh) | Carbon Intensity (gCO₂/kWh) | Carbon Price ($/ton) |
| --- | --- | --- | --- | --- | --- |
| 🇰🇷 Korea (this DT) | Tandem | 1,340 | 90 | 415 | 20 |
| 🇺🇸 USA | c-Si Bifacial | 1,800 | 65 | 370 | 0 |
| 🇨🇳 China | c-Si | 1,500 | 55 | 555 | 10 |
| 🇯🇵 Japan | c-Si + Perovskite | 1,200 | 150 | 450 | 5 |
| 🇩🇪 Germany | c-Si + Agri-PV | 1,050 | 180 | 350 | 55 |

Sources: KMA, NREL NSRDB, CMA, JMA AMeDAS, DWD (weather); KEPCO, EIA, NDRC, METI, Destatis (prices); KPX, EPA eGRID, MEE, MOE, UBA (emission factors).

### 5.4 Global Hyperscaler Strategy Comparison

| CSP | Strategy | Energy Mix | LCOE (₩/kWh) | Carbon (tCO₂/MWh) | Grid Dependency |
| --- | --- | --- | --- | --- | --- |
| Google | Co-located Renewables | Solar 50%, Wind 30%, Grid 20% | 64.0 | 0.092 | 20% |
| Amazon | Dedicated Gas | Gas 65%, Battery 15%, Grid 20% | 97.5 | 0.259 | 20% |
| Meta | Behind-the-Meter Gas | Gas 70%, Grid 30% | 87.0 | 0.259 | 30% |
| Microsoft | Grid Partnership | Grid 60%, Wind 25%, Solar 15% | 69.5 | 0.276 | 60% |
| Samsung SDS | Grid Dependent | Grid 85%, Solar 10%, ESS 5% | 79.0 | 0.391 | 85% |
| Naver | Hybrid | Grid 60%, FC 25%, Solar 15% | 74.5 | 0.276 | 60% |

────────────────────────────────────────────────────────────

## 6. Discussion

### Key Strengths

Comprehensive framework: 13+3 modules covering the full value chain from weather to investment decision

Frequency-based HESS: The 6-layer architecture with μs-to-seasonal time constants is academically novel and practically relevant for AIDC power quality requirements

Transparent economics: The "no-exaggeration principle" with Monte Carlo uncertainty quantification builds credibility with reviewers and investors

Industry-specific analysis: Named CSP profiles (Samsung, SK, Naver, Kakao) and global hyperscaler strategy comparison demonstrate practical applicability

### Limitations

Lumped-parameter model: Spatial distribution effects (e.g., partial shading, cable losses) are not captured

Deterministic LP dispatch: Stochastic MPC or robust optimization would better handle forecast uncertainty

Normal distribution assumption in MC: Fat-tailed distributions (log-normal, jump-diffusion) are more appropriate for energy/carbon prices

Base case IRR ~4.5%: Below typical private investment thresholds; the combined scenario (12–15%) relies on favorable policy assumptions

Solar Battery STH 57.6%: Theoretical ideal; laboratory state-of-the-art is ~20% for conventional pathways

### Future Work

PINN (Physics-Informed Neural Network) integration for Tier 2 dispatch

LSTM/Transformer-based PV and load forecasting

Stochastic MPC for Tier 2 optimization

Log-normal/jump-diffusion Monte Carlo

Detailed partial shading and cable loss models

SOEC/SOFC high-temperature pathway as alternative to PEM

────────────────────────────────────────────────────────────

## 7. Conclusions

CEMS Digital Twin v5 provides a validated, multi-scale simulation platform for 100 MW AIDC renewable microgrids. The 6-layer HESS with frequency-based dispatch, 3-tier AI-EMS with LP optimization, and Monte Carlo economic analysis constitute a comprehensive toolkit for system design, operation, and investment decisions. With 92/92 tests passing and an advisory board rating of A−, the platform is ready for demonstration to a 10-member faculty panel and serves as a foundation for subsequent publications targeting Applied Energy or IEEE Transactions on Smart Grid.

────────────────────────────────────────────────────────────

## 8. References

De Soto, W., Klein, S. A., & Beckman, W. A. (2006). Improvement and validation of a model for photovoltaic array performance. Solar Energy, 80(1), 78–88.

IEC 61215:2021. Terrestrial photovoltaic (PV) modules — Design qualification and type approval.

IEC 61853-1:2011. Photovoltaic (PV) module performance testing and energy rating.

IRENA (2024). Green Hydrogen Cost Reduction: Scaling Up Electrolysers to Meet the 1.5°C Climate Goal.

U.S. DOE (2024). Hydrogen Program Record: PEM Fuel Cell System Cost.

IEA (2023). Global Hydrogen Review 2023.

BloombergNEF (2025). Hydrogen Levelized Cost Report.

Nature Reviews Materials (2025). Next-generation anodes for sodium-ion batteries. doi:10.1038/s41578-025-00857-4.

Nature Communications (2026). Solar battery for on-demand hydrogen production. doi:10.1038/s41467-026-68342-2.

NREL (2024). Annual Technology Baseline (ATB).

IRENA (2024). Renewable Power Generation Costs in 2023.

Fraunhofer ISE (2024). Levelized Cost of Electricity — Renewable Energy Technologies.

Lazard (2024). Levelized Cost of Storage Analysis — Version 9.0.

KEPCO (2024). 전기요금표 — 산업용(갑) II.

KPX (2024). 전력시장 운영 실적 및 보조서비스 시장 보고서.

EPRI (2023). The Value of Distributed Energy Resources.

────────────────────────────────────────────────────────────

CEMS Digital Twin v5 Technical Document (English)

Generated: 2026-03-02